## Common failures
Most frequent failure type for each component.
System | Component | Frequent Failure Type | Cause | Effect | Result | Mitigation
Rotor System | Blades | Fatigue cracks, erosion, lightning damage | Cyclic loading, rain/sand erosion, lightning strikes | Surface cracking, delamination | Reduced aerodynamic efficiency, rotor imbalance | Apply erosion-resistant coatings, lightning protection, routine drone inspection
| Blade Root | Bolt loosening, fatigue cracking | High cyclic stresses, vibration | Loss of preload, micro-cracks | Structural instability, detachment risk | Torque verification, bolt retightening, NDT inspections
| Pitch Mechanism (Hydraulic/Electric Actuators, Bearings) | Bearing wear, actuator leakage/failure | Lubricant contamination, corrosion, overheating | Delayed or inaccurate pitch movement | Overspeed or load imbalance | Regular lubrication, seal checks, sensor monitoring
| Lightning Protection System | Corrosion, cable disconnection | Moisture ingress, poor grounding | Reduced lightning conduction | Structural damage after strike | Regular continuity checks, grounding resistance testing
| Hub | Crack formation, grease leakage | Fatigue, poor lubrication | Structural imbalance | Increased vibration, safety risk | Regular ultrasonic inspection, grease renewal
| Pitch Drives | Gear wear, motor overheating | Continuous operation, high torque | Reduced pitch movement accuracy | Loss of aerodynamic control | Periodic lubrication, temperature monitoring
Nacelle (Main Housing) | Main Shaft (Low-Speed Shaft) | Misalignment, fatigue | Improper assembly, vibration | High bearing stress | Gearbox coupling failure | Alignment verification, vibration analysis
| Bearings | Wear, pitting, overheating | Contamination, poor lubrication | Friction increase | Shaft seizure, failure | Oil filtration, condition monitoring
| Gearbox (Planetary/Helical) | Gear tooth wear, bearing failure | Oil contamination, overloading | Vibration, noise | Power transmission loss | Oil analysis, vibration diagnostics
| Gearbox Lubrication System | Oil leaks, pump failure | Seal damage, clogging | Low lubrication pressure | Gear overheating | Regular oil change, filter replacement
| Direct-Drive System | Bearing overheating, stator faults | Cooling loss, electrical overload | Increased heat | Reduced efficiency, shutdown | Temperature sensors, cooling checks
| Generator (SCIG, DFIG, PMSG) | Bearing failure, insulation degradation | Electrical imbalance, heat | Increased friction | Reduced power output | Periodic cleaning, thermal inspection
| Brake System (Disc/Hydraulic) | Pad wear, pressure loss | Friction wear, fluid leaks | Reduced braking power | Overspeed risk | Fluid check, brake pad replacement
| Yaw System (Motors, Bearings, Brakes) | Motor failure, brake wear | Continuous motion, corrosion | Yaw misalignment | Efficiency loss, safety risk | Lubrication, brake inspection
| Cooling System (Air/Liquid) | Fan failure, blockage | Dust, clogging | Overheating | Component damage | Filter cleaning, fan replacement
| Lubrication System (Pumps, Filters) | Pump failure, clogging | Oil contamination | Reduced flow | Gear damage | Scheduled oil/filter maintenance
| Sensors (Vibration, Temperature) | Signal loss, drift | Moisture, heat | Incorrect readings | Missed failure detection | Sensor calibration, redundancy systems
Tower System | Structure | Corrosion, cracks | Environmental exposure | Weak joints, weld fatigue | Collapse risk | Coating maintenance, ultrasonic inspection
| Internal Ladders/Safety Systems | Corrosion, wear | Moisture, mechanical stress | Reduced safety | Worker hazard | Material upgrade, periodic inspection
| Service Lift | Motor or cable failure | Overuse, poor maintenance | Lift stall | Maintenance access loss | Motor testing, cable replacement
| Cable Trays | Loosening, corrosion | Vibration, humidity | Cable sagging | Electrical hazards | Fastener tightening, anti-corrosion treatment
| Platforms/Rest Stations | Structural looseness | Vibration | Safety risk | Fall hazard | Bolt tightening, visual checks
| Tower Lighting | Bulb or circuit failure | Electrical fault | Loss of visibility | Non-compliance | Replace bulbs, check wiring
| Foundation | Cracks, settling | Soil erosion, fatigue | Structural shift | Tower tilt or collapse | Ground survey, reinforcement
Electrical System | Power Electronics (Converter/Inverter) | IGBT failure, capacitor aging | Overvoltage, heat | Electrical short | Converter trip | Cooling system maintenance, surge protection
| Control Boards | Burnout, moisture damage | Voltage spikes, condensation | Signal loss | Turbine stoppage | Sealing, grounding, routine test
| Transformer | Oil leak, insulation failure | Overload, heat | Arcing | Power loss | Oil testing, thermal imaging
| Switchgear | Contact wear, breaker trip | Overcurrent | Electrical fault | Power interruption | Contact inspection, breaker test
| Cabling | Insulation degradation | Moisture, abrasion | Short circuit | Fire or outage | Cable inspection, protective conduit
Control & Safety Systems | SCADA System | Software or comms error | Network fault | Data loss | Remote control loss | Software update, signal redundancy
| PLC | Module failure, logic error | Power surge | Control error | Wrong turbine action | Backup modules, surge protectors
| Remote Monitoring | Communication loss | Antenna damage | No signal | Lost diagnostics | Regular link testing
| Anemometer | Bearing failure, icing | Weather, aging | Inaccurate wind speed | Control error | Heated sensors, calibration
| Wind Vane | Misalignment, corrosion | Wind fatigue | Wrong direction | Yaw error | Alignment, protective coating
| Pitch Control System | Software fault, sensor drift | Electrical issue | Wrong pitch angle | Overspeed | Firmware updates, sensor check
| Yaw Control System | Feedback sensor fault | Wiring issue | Poor alignment | Energy loss | Feedback loop check
| Emergency Stop | Contact wear | Use over time | Button failure | Safety hazard | Replace switch, test quarterly
| Backup Power System | Battery degradation | Aging | Low capacity | Control loss during outage | Battery testing, replacement
| Lightning Protection | Corrosion, disconnection | Moisture, poor contact | Ineffective grounding | Damage during strike | Continuity testing, grounding maintenance
Auxiliary Systems | Hydraulic System | Oil leaks, pressure loss | Seal wear, contamination | Low pressure | Brake/pitch failure | Filter change, oil check
| Heating System | Heater burnout | Overload, age | Low nacelle temp | Reduced performance | Replace elements, thermostat test
| Blade De-Icing System | Heater element burnout | Ice load, electrical fault | Ice buildup | Power loss | Maintenance during winter
| Cooling Fans/Ventilation | Fan bearing failure | Dust, overload | Overheating | Component failure | Fan cleaning, vibration check
| Fire Suppression System | Sensor or pressure fault | Age, corrosion | Non-function | Fire spread | Inspection, refill, sensor test

## Common Maint. Tech.
Most common maintenance technique for each component type
System | Component | Most Common Maintenance Technique | Typical Maintenance Activity
Rotor System | Blades | Preventive / Predictive | Regular visual & drone inspections, ultrasonic/NDT for cracks, leading-edge recoating
| Blade Root | Preventive | Bolt torque checks, corrosion treatment, ultrasonic inspections
| Pitch Mechanism (Hydraulic/Electric Actuators, Bearings) | Predictive | Vibration & oil analysis, seal and actuator monitoring
| Lightning Protection System | Preventive | Continuity testing, grounding inspection
| Hub | Preventive | Grease renewal, bolt tightening, visual crack checks
| Pitch Drives | Predictive | Motor temperature & torque monitoring, gear inspection
Nacelle (Main Housing) | Main Shaft (Low-Speed Shaft) | Predictive | Vibration analysis, alignment verification
| Bearings | Predictive | Oil debris analysis, temperature & vibration monitoring
| Gearbox (Planetary/Helical Stages) | Predictive | Oil analysis, vibration & acoustic monitoring
| Gearbox Lubrication System | Preventive | Oil and filter change schedule, leak inspection
| Direct-Drive System | Predictive | Electrical and temperature monitoring, thermal imaging
| Generator (SCIG, DFIG, PMSG) | Predictive | Insulation resistance testing, bearing temperature trending
| Brake System (Disc/Hydraulic/Emergency) | Preventive | Brake pad inspection, hydraulic fluid replacement
| Yaw System (Motors, Bearings, Brakes) | Predictive | Vibration monitoring, lubrication, brake torque testing
| Cooling System (Air/Liquid) | Preventive | Fan cleaning, filter replacement, coolant checks
| Lubrication System (Oil Pumps, Filters) | Preventive | Oil sampling, filter change, pump operation test
| Sensors (Vibration, Temperature, Strain, Oil Quality) | Preventive | Calibration, sensor function testing
Tower System | Tower Structure | Preventive | Visual corrosion inspection, bolt tightening, NDT on welds
| Internal Ladders and Safety Systems | Preventive | Safety gear inspection, ladder alignment check
| Service Lift | Preventive / Corrective | Cable lubrication, motor inspection, brake checks
| Cable Trays | Preventive | Fastening inspection, corrosion checks
| Platforms / Rest Stations | Preventive | Structural inspection, bolt tightening
| Tower Lighting | Corrective | Bulb or circuit replacement as needed
| Foundation | Predictive / Preventive | Crack monitoring, settlement survey
Electrical System | Power Electronics (Converters, Inverters) | Predictive | Thermal imaging, capacitor health monitoring
| Control Boards | Corrective / Preventive | Dust removal, voltage stability testing
| Transformer | Predictive | Oil dielectric testing, infrared thermal scanning
| Switchgear | Preventive | Contact resistance test, breaker operation check
| Cabling | Preventive | Insulation resistance test, connector inspection
Control & Safety Systems | SCADA System | Preventive | Software update, data backup, network test
| PLC (Programmable Logic Controllers) | Preventive | Firmware updates, signal validation
| Remote Monitoring & Communication Modules | Preventive / Corrective | Signal test, antenna alignment
| Anemometer | Preventive | Calibration, bearing lubrication
| Wind Vane | Preventive | Alignment verification, corrosion control
| Pitch Control System | Predictive | System diagnostics, sensor calibration
| Yaw Control System | Predictive | Motor current and torque monitoring
| Emergency Stop Buttons | Preventive | Contact testing, functional check
| Backup Power Systems (Batteries, Supercapacitors) | Preventive | Voltage testing, battery replacement
| Lightning Protection System | Preventive | Continuity and grounding resistance measurement
Auxiliary Systems | Hydraulic System (Pitch/Yaw/Braking) | Predictive | Oil condition & pressure monitoring, leak detection
| Heating Systems (Nacelle Heaters) | Corrective / Preventive | Function test, thermostat replacement
| Blade De-Icing Systems | Preventive | Electrical testing, heating element inspection
| Cooling Fans and Ventilation | Preventive | Cleaning, vibration check, bearing lubrication
| Fire Suppression System | Preventive | Pressure test, sensor calibration, extinguisher refill

## Rank Failure
Ranking of all components based on likelihood for failure
Rank | System | Component | Failure Likelihood | Reason for High/Low Failure Rate
1 | Rotor System | Blades | Very High | Subject to wind loads, fatigue, erosion, lightning; frequent surface and structural damage
2 | Nacelle | Gearbox (planetary/helical) | Very High | Complex moving parts, lubrication contamination, bearing and gear wear
3 | Rotor System | Pitch Mechanism (hydraulic/electric actuators, bearings) | High | High cyclic motion, contamination, hydraulic leaks, actuator burnout
4 | Nacelle | Bearings (main and gearbox) | High | Constant rotation, high stress, lubrication degradation | Summary of Categories
5 | Nacelle | Generator (SCIG/DFIG/PMSG) | High | Electrical and thermal stress, insulation and bearing failures | Frequency | Category
6 | Nacelle | Yaw System (motors, bearings, brakes) | Medium–High | Continuous motion, corrosion, brake wear | High | Rotor blades
7 | Rotor System | Pitch Drives | Medium–High | Gear/motor wear, control faults, overheating | High | Gearboxes
8 | Nacelle | Brake System (disc, hydraulic, emergency) | Medium | Pad wear, fluid leaks, actuator failure | High | Pitch Systems
9 | Electrical System | Power Electronics (Converters/Inverters) | Medium | IGBT failure due to heat and voltage transients | Medium | Generators
10 | Control & Safety | Pitch Control System | Medium | Software or feedback sensor errors | Medium | Yaw Systems
11 | Control & Safety | PLC / SCADA Systems | Medium | Communication loss, sensor faults, firmware errors | Medium | Brakes and converters
12 | Nacelle | Cooling System (air/liquid) | Medium | Fan failure, filter clogging, overheating | Lowest | Tower
13 | Nacelle | Lubrication System (pumps/filters) | Medium | Filter clogging, oil leaks | Lowest | Foundation
14 | Electrical | Cabling (HV/control/fiber) | Medium | Insulation breakdown, vibration wear | Lowest | Safety Systems
15 | Nacelle | Main Shaft (low-speed) | Medium–Low | Fatigue or misalignment; less frequent but severe when occurs
16 | Tower | Tower Lighting | Medium–Low | Electrical burnout; low-cost frequent replacement
17 | Control & Safety | Sensors (Anemometer, Wind Vane) | Medium–Low | Corrosion, icing, signal loss
18 | Auxiliary | Hydraulic System (for pitch/yaw/brake) | Medium–Low | Leakage, seal wear, pressure drops
19 | Electrical | Transformer | Low | Well protected, fails mostly due to overheating or oil issues
20 | Tower | Structure (steel/concrete) | Low | Designed for long life; failures due to fatigue or corrosion are rare
21 | Tower | Foundation | Low | Rare, occurs from soil settlement or cracking over decades
22 | Control & Safety | Emergency Stop / Backup Power | Low | Passive components, rare failures
23 | Auxiliary | Cooling Fans & Ventilation | Low | Minor wear issues, easy to replace
24 | Rotor System | Lightning Protection System | Low | Simple system; only fails when corroded or disconnected
25 | Tower | Service Lift / Ladders / Platforms | Low | Mechanical wear, corrosion - negative impact safety maintenance prevents failures
26 | Auxiliary | Fire Suppression / Heating / De-Icing Systems | Low | Typically redundant; only fail under extreme weather conditions