## Component breakdown
System | Components | Failure | Severity & Justification |  | Failure Cause | Root Cause | Occurance & Justification |  | Detection & Justification |  | RPN | Risk Level
Rotor System | Blades | Leading edge erosion | 10 | Blade failure can lead to catastrophic damage. | rain, hail, sand, and dust erode the blade’s outer coating | High-speed rain/particle impact during normal operation, especially at blade tip speeds of 60–80 m/s | 7 | moderate–high. Field studies report visible leading-edge erosion on ~20–30 % of blades within 5 years, especially in wet or coastal climates. | 9 | detection can be difficult (internal cracks) | 630 | High
| Blade root | Fatigue cracking in root bolts or laminates | 10 | Critical structural failure point; | Repeated cyclic loading from wind gusts causes micro-cracks in composite laminates or root bolts/flanges | High‐cycle fatigue from turbulence, frequent start/stop cycles, and yaw misalignment | 4 | Probability of data:Moderate (~10–15 % over 15–20 yr life), higher in sites with high turbulence intensity or older bonding designs | 8 | near-impossible to detect early without advanced tech | 320 | High
| Pitch mechanism (hydraulic/electric actuators, bearings) | Oil contamination | 7 | Failure affects wind capture and load control. | sticky servo/pilot valves, slow or drifting pitch, accumulator/seal wear | Inadequate filtration or overdue filters; breached seals/breathers letting dust/moist air in; condensation from daily temp swings; dirty fill/transfer practices; wrong oil or mixed oils after repairs | 8 | Probability of Data: Most common hydraulic issue. Expect ~40–60% of pitch-hydraulic faults to involve contamination at some point; | 5 | Moderate detectability via SCADA or vibration monitoring. | 280 | Medium
| Lightning protection system | Receptor wear or damage | 9 | Failure can cause blade burns or fire. | Repeated lightning strikes or erosion from rain, hail, and UV exposure degrade the receptor surface or loosen hardware | Natural strike frequency, inadequate material hardness, poor maintenance access | 3 | Probability of Data: High in thunderstorm regions (20–40 % of blades show receptor wear within 5 years). | 9 | detection is usually post-failure. | 243 | Medium
| Hub | Structural cracking of hub casting/welds | 9 | Failure is severe | High cyclic bending loads from gusts or rotor imbalance produce micro-cracks in the cast or welded hub body | Casting porosity, residual welding stresses, or operating beyond design wind regime | 4 | Probability of Data: Low–Moderate (~3–8 % over 20-yr life); higher on older designs or sites with extreme turbulence. | 7 | Detection is challenging without teardown | 252 | Medium
| Pitch drives | Gear wear or pitting | 8 | Drives blade pitch—failure limits control. | Continuous oscillatory motion of drive gearbox during frequent pitch corrections | Inadequate or degraded grease/oil, misalignment of motor and ring gear, overload from abrupt braking or high turbulence | 6 | Probability of Data: Moderate (~15–25 % over 10-15 yrs) depending on turbulence and lubrication quality. | 8 | Easier to detect than internal pitch mechanism faults. | 384 | High
Nacelle (Main Housing) | Main shaft (low-speed shaft) | Bearing surface fatigue | 10 | Failure leads to total loss of drivetrain functionality. | High cyclic loads and bending moments from rotor torque | Misalignment between main bearing and gearbox, inadequate or degraded lubrication film, contamination of grease/oil, high turbulence events | 4 | Moderate (~15–25 % over 20-yr life); higher in high-turbulence or offshore sites. | 8 | hard to detect fatigue early. | 320 | High
| Bearings | Main shaft (main bearing) surface pitting & spalling | 9 | High wear-and-tear component. | Rolling contact fatigue under high cyclic loads | Contaminated or degraded lubricant, misalignment between rotor hub and gearbox, overload during extreme winds or emergency stops | 6 | Probability of Data: Moderate (~10–20 % over 20-yr life); higher in turbines with high turbulence or poor alignment control | 3 | Detectable via vibration analysis, but still a leading failure cause. | 162 | Medium
| Gearbox (planetary, helical stages) | Gear tooth pitting / micropitting | 10 | Catastrophic if it fails; | High contact stress from continuous torque transmission | Inadequate lubrication film, misalignment of planetary or helical gears, contaminated oil increasing wear particles | 8 | Probability of Data: High (~30–40 % over 20-year life)—most common gearbox failure mode | 5 | some detection possible (noise, oil debris). | 400 | High
| Gearbox lubrication system | Oil pump failure | 4 | Indirect failure of gearbox if oil quality/flow is compromised. | Loss of oil flow or pressure | Pump motor burnout, bearing wear, cavitation from clogged suction strainer, low oil level, or air ingress | 5 | Probability of Data: Moderate (~10–15 % over 10 yrs); higher if oil cleanliness is poor | 3 | Has pressure, temperature, flow, and oil-quality sensors that detect most issues early. | 60 | Low
| Direct-drive system (if applicable) | Generator bearing wear or false brinelling | 9 | Very severe if failed. Less complex than gearbox but still hard to repair. Fewer moving parts. | High radial/axial loads and vibration during low-speed rotation | Insufficient or degraded grease, contamination from moisture, long standstill periods causing micro-movement | 4 | Probability of Data: Moderate (~15–25 % over 15-20 yrs), higher in offshore/humid climates | 4 | Fewer moving parts; failures tracked via vibration & temperature monitoring but subtle electrical faults can be harder to detect. | 144 | Low
| Generator (SCIG, DFIG, PMSG) | Stator winding insulation breakdown | 4 | Moderate severity unless fire occurs. | Overheating, electrical surges, or partial discharge in high-voltage coils | Prolonged thermal stress from high reactive power or poor cooling, contamination with moisture/oil, voltage transients during switching or lightning events | 6 | Probability of Data: Moderate (~10–20 % over 15–20 yrs), higher in humid or offshore climates. | 5 | SCADA and thermal sensors help detect issues. | 120 | Low
| Brake system (disc, hydraulic, emergency) | Disc pad wear or glazing | 7 | Failure in emergency braking is dangerous. | Repeated braking during high-wind stops and service operations | Normal friction wear; misalignment of caliper; excessive heat from long braking intervals | 8 | Probability of Data: High (~30–40 % pad replacement required within 3–5 yrs) depending on site wind regime | 4 | detection isn’t always immediate. | 224 | Medium
| Yaw system (motors, bearings, brakes) | overheating or winding failure | 9 | Failure causes misalignment → efficiency loss or structural stress. Some SCADA data can help. | Excessive duty cycle when tracking rapidly changing wind direction | Cooling fan/filter clogging, high ambient nacelle temperatures, gearbox drag increasing torque demand | 6 | Probability of Data: Moderate (~10–20 % over 15 yrs) depending on climate and service intervals | 5 | Yaw errors detected by position sensors & SCADA, but bearing wear is not easily caught early. | 270 | Medium
| Cooling system (air/liquid, heat exchangers) | Fan motor failure (air-cooling system) | 5 | Affects generator/gearbox longevity. | Overheating of generator, gearbox, or converter due to loss of airflow | Fan motor bearing wear, electrical short, clogged filters increasing current draw | 6 | Probability of Data: Moderate (~15–25 % over 10 yrs)—higher in dusty or offshore environments | 3 | Detectable with thermal monitoring. | 90 | Low
| Lubrication system (oil pumps, filters) | Pump wear or loss of pressure | 6 | Indirectly causes drivetrain wear. | Continuous high-load operation and contamination of lubricant | Abrasive particles or water in oil; running dry due to low oil level; cavitation from restricted suction; misalignment of pump shaft | 5 | Probability of Data: Moderate (~10–20 % over 10–15 yrs) depending on oil cleanliness and pump design | 3 | Detection via pressure/flow/oil sensors. | 90 | Low
| Sensors (vibration, temperature, strain, oil quality) | Vibration sensor (accelerometer) drift or failure | 6 | Their failure reduces system observability → hidden failures. Often overlooked but risky. | Continuous high-frequency vibration and temperature cycling | Piezoelectric element fatigue, loose mounting, connector corrosion, or water ingress | 6 | Probability of Data: Moderate (~15–25 % over 10 yrs) depending on vibration severity and humidity | 2 | Sensors are self-monitored; failure is usually detected by signal loss or anomaly flags. | 72 | Low
Tower System | Tower structure (steel, concrete, hybrid, lattice) | Fatigue cracking in steel shell or flange welds | 10 | Catastrophic failure if structural collapse occurs (entire turbine loss). | Cyclic loading from wind gusts, rotor imbalance, and start/stop operations | High turbulence, inadequate weld quality, stress concentrations at door openings or flange joints | 6 | Probability of Data: Moderate (~10–15 % over 20 years) depending on turbulence class and weld quality | 8 | Crack formation, fatigue, or corrosion progress slowly and often requires visual inspection to detect. | 480 | High
| Internal ladders and safety systems | Ladder rung or rail fatigue cracking | 9 | Failure can cause complete turbine loss or tilt. | Repeated climbing loads and tower vibration over years of service | Weld defects, material fatigue, or corrosion at weld joints and bolt connections | 3 | Probability of Data: Low–Moderate (~5–10 % over 20 yrs), higher in high-vibration or offshore environments | 9 | Failures (corrosion, loose mounts) are rarely monitored electronically; detected only by manual inspection. | 243 | Medium
| Service lift | Hoist motor overheating or winding failure | 5 | Affects technician access and maintenance efficiency, not turbine operation. | Continuous or overloaded operation of the lift motor | Excess passenger/cargo weight, frequent starts/stops, blocked ventilation, or worn bearings increasing motor load | 5 | Probability of Data: Moderate (~10–20 % over 10 yrs) depending on duty cycle and climate | 6 | Electrical faults often monitored, but mechanical cable/wear failures rely on inspection. | 150 | Low
| Cable trays | Cable insulation damage / chafing | 6 | Failure (e.g., broken rung, safety rail malfunction) can cause injury or rescue issues. | Continuous vibration of the tower and oscillation of the power/control cables inside the tray | Sharp tray edges, missing grommets, improper cable tie spacing, and insufficient slack to absorb movement | 8 | Probability of Data: High (~30–40 % of turbines within 10 yrs) if trays are not routinely inspected in high-vibration sites | 8 | No real-time monitoring; physical damage detected only during inspection. | 384 | High
| Platforms/rest stations | Corrosion of platform grating/ rails/ladder connections | 4 | Structural or integrity issues could cause minor injuries or hinder access; | Condensation, humidity inside the tower, salt spray (offshore/coastal), leaking hatches | Inadequate surface coating or damaged galvanization; insufficient ventilation; standing water | 6 | Probability of Data: Moderate (~20–30 % over 10 years onshore, 40–50 % offshore) | 9 | Static structures; no sensors. Issues like rust or loosened bolts require inspection. | 216 | Medium
| Tower lighting (aviation compliance) | LED/Beacon Lamp Burnout or Dimming | 7 | Failure could lead to cable damage or fire risk, but not catastrophic; | Aging of LED modules or xenon flash tubes | Normal lumen depreciation, power surges, or thermal stress from poor heat dissipation | 5 | Probability of Data: Moderate (~15–25 % over 5–7 yrs) depending on environment and operating hours | 3 | Lighting has failure alarms and redundant circuits. | 105 | Low
| Foundation (gravity, pile, monopile, jacket, tripod, floating) | Corrosion of steel components | 10 | Critical — any settlement, cracking, or failure leads to turbine collapse or decommissioning | Continuous exposure to seawater and oxygen promotes electrochemical attack | Damaged protective coatings, depleted cathodic protection (anodes), poor paint application, or coating holidays | 7 | Probability of Data: High offshore (≈40–60% show measurable corrosion within 10 yrs); lower onshore gravity foundations. | 9 | Failure modes like soil interaction, corrosion, scour often not detected until structural inspections | 630 | High
Electrical System | Power electronics (converters, rectifiers, inverters) | IGBT/Power transistor failure | 9 | A failure leads to loss of power conversion and immediate turbine shutdown; high cost and downtime. | Over-current or over-voltage during grid faults or switching transients. | Lightning strikes, poor surge suppression, inadequate thermal management, or control software malfunction | 5 | Probability of Data: Moderate (~10–20 % over 10 yrs) depending on site lightning incidence and grid quality. | 4 | Thermal sensors and fault codes detect many issues, but some IGBT failures occur catastrophically. | 180 | Medium
| Control boards | Component overheating or burnout | 7 | Can cause control or communication loss but may be isolated or redundantly managed. | High ambient nacelle temperature, poor ventilation, or overloaded circuits. | Clogged filters or failed cooling fans; undersized power supply; dust accumulation acting as an insulator. | 5 | Probability of Data: Moderate (~10–20 % over 10 yrs), higher in hot or dusty climates. | 4 | Self-monitoring and fault codes catch many failures | 140 | Low
| Transformer (step-up, nacelle or tower base) | Insulation breakdown / winding short | 10 | Catastrophic — complete turbine downtime and possible fire hazard; costly to replace. | Electrical overstress or thermal aging of winding insulation | Overvoltage from lightning or switching surges, partial discharge from moisture, long-term thermal degradation | 4 | Probability of Data: Moderate (~10–20 % over 15–20 yrs); higher in humid/offshore environments. | 6 | Thermal and oil sensors detect some issues, but winding insulation faults may go unnoticed | 240 | Medium
| Switchgear (circuit breakers, disconnect switches) | Contact wear / erosion | 8 | Failure can isolate turbine or cause electrical faults; moderate-to-high repair time. | High number of switching operations and normal arcing during load interruption. | Frequent breaker operations from grid disturbances, capacitor switching, or excessive load cycling. | 6 | Probability of Data: Moderate (~15–25 % within 10 yrs) depending on breaker duty cycle. | 3 | Most failures detected by trip signals or SCADA alarms. | 144 | Low
| Cabling (high-voltage, control, fiber optic) | High-voltage (HV) power cable insulation breakdown | 6 | Failure may cause data loss or local electrical issues but usually not catastrophic if isolated. | Electrical stress, partial discharge, or moisture ingress at terminations. | Age-related insulation degradation, poor cable routing causing bending radius violations, or damaged sheath from vibration/chafing. | 4 | Probability of Data: Moderate (~10–20 % over 20 yrs)—higher in humid/coastal climates or turbines with frequent yaw movement. | 7 | Shorts/opens detected, but insulation degradation is hard to detect early | 168 | Medium
Control & Safety Systems | SCADA system | Communications loss between turbine/SCADA master | 7 | Affects monitoring and data logging; turbine can still operate locally but with limited oversight. | Physical cable damage, radio link outage, modem/router crash, fiber cut | Environmental damage, poor routing, aging comms hardware, single point-of-failure network design | 9 | Probability of Data: High — ~90% (SCADA/historian will usually show link loss quickly) | 2 | Highly monitored; communication failures noticed instantly | 126 | Low
| PLC (programmable logic controllers) | CPU crash / hang / freeze | 9 | Central control failure stops turbine operation; safety and performance compromised. | Software bug, memory leak, corrupted task, unexpected input | Poor software QA, outdated firmware, insufficient memory margin | 9 | Probability of Data: High (~80–95%) — watchdog/heartbeat and restart logs usually recorded | 3 | Programmable controllers self-test and flag most faults | 243 | Medium
| Remote monitoring & communication modules | Total communication loss (no data link) | 6 | Loss of remote visibility but local turbine control remains functional. | Cable cut, modem/router crash, antenna damage, power loss | Environmental damage, poor routing, single-point-of-failure design | 8 | Probability of Data: High (~85–95%) — heartbeats, data age alarms quickly visible in SCADA | 4 | Signal issues detected quickly, but intermittent failures can be harder to detect. | 192 | Medium
| Anemometer | Signal loss or dropout | 7 | Inaccurate wind data affects turbine performance and safety systems (pitch/yaw control). | Interruption of wind speed signal to turbine controller. | Broken cables, connector corrosion, or slip-ring faults in the nacelle. | 6 | Probability of Data: Moderate (~10–20 % within 5 yrs) | 4 | Failure detected via signal loss or comparison to redundant sensors. | 168 | Medium
| Wind vane | Signal drift or inaccurate wind direction | 7 | Impacts yaw control accuracy but turbine can still operate with conservative fallback modes. | Sensor aging or misalignment. | UV degradation of plastic body, bearing wear, calibration drift in potentiometer/encoder. | 8 | Probability of Data: High (~30–40 % after 5–7 years) without calibration program. | 4 | Detected by inconsistency with other signals or yaw errors. | 224 | Medium
| Pitch control system | PLC/Controller fault | 10 | Critical—failure can lead to overspeed or blade damage; turbine must shut down. | Internal hardware fault, firmware bug, or watchdog reset. | Component aging, power supply dips, or corrupted firmware. | 5 | Probability of Data: Moderate (~10–15 % over 10 years), higher in older fleets | 4 | Blade-angle sensors and hydraulic pressures detect most faults. | 200 | Medium
| Yaw control system | Yaw motor/drive overheating or burnout | 9 | Improper alignment reduces energy yield and can cause structural stress or damage. | Excessive current draw during high wind yawing or continuous correction. | Poor ventilation in nacelle, clogged filters, motor bearing wear, misalignment of pinion with yaw gear. | 4 | Probability of Data: Moderate (~10–15 % over 10 years), depending on actuation frequency. | 5 | Position sensors detect errors but mechanical wear detection is weaker. | 180 | Medium
| Emergency stop buttons | Contact wear or pitting | 8 | Failure to engage during emergency is high-risk for personnel and equipment safety. | Frequent actuations or arcing when interrupting control voltage. | Mechanical wear of silver contacts; lack of arc suppression; poor contact material. | 4 | Probability of Data: Moderate (~10–15 % over 10 years), depending on actuation frequency. | 2 | Self-testing circuits detect most failures | 64 | Low
| Backup power systems (batteries, supercapacitors) | Battery capacity loss (sulfation / aging) | 8 | Loss of emergency pitch control or braking function during power loss; serious risk. | Normal cycle aging, deep discharges, and high temperature. | Lead-acid batteries suffer from sulfation of plates and electrolyte stratification. | 8 | Probability of Data: High. Nearly all battery-based systems show significant degradation within 2–4 years of service | 6 | Charge-state monitored, but internal degradation is less detectable. | 384 | High
| Lightning protection system (receptors, down conductors, grounding) | Receptor erosion or damage | 10 | Failure can lead to catastrophic blade or nacelle damage and full system loss. | Direct lightning strikes exceeding design limits or repeated smaller strikes. | Natural erosion from high-energy events, poor bonding to blade laminate, or manufacturing defect | 7 | Probability of Data: High (~30–40 % of blades show receptor wear by 5 years in high-storm regions) | 9 | Often no real-time monitoring; only discovered during inspections | 630 | High
Auxiliary Systems | Hydraulic system (for pitch, yaw, braking) | Oil contamination (particles / water) | 10 | Critical — controls pitch and braking; loss can cause overspeed or total failure requiring shutdown. | Dirty fill practices, seal failures, condensation, or worn pumps introducing particles. | Inadequate filtration, clogged filters, or missing/desiccant breathers. | 8 | Probability of Data: High (~40–60 % of hydraulic faults) | 5 | Pressure sensors catch some issues but leaks can be slow and hard to catch | 400 | High
| Heating systems (nacelle heaters) | Thermostat or temperature sensor malfunction | 5 | Failure leads to cold-related issues but not direct turbine shutdown; affects reliability and component life. | Incorrect temperature regulation (overheating or underheating) | Sensor drift, wiring corrosion, or failed thermostat contacts | 4 | Probability of Data: Moderate (~10–15 % in 10 yrs) | 4 | Monitored through temperature feedback | 80 | Low
| Blade de-icing systems (electrical, hot air) | Heating element burnout (electrical mats/resistive wires) | 8 | Failure leads to ice buildup, reducing efficiency and possibly causing imbalance or blade damage. | Overheating due to poor thermal contact or control fault. | Local hot spots, insulation degradation, power surges. | 6 | Probability of Data: Moderate–High (~20–30 % over 10 yrs) | 5 | Electrical monitoring helps, but partial failures not always obvious | 240 | Medium
| Cooling fans and ventilation | Fan motor burnout | 7 | Overheating of nacelle components (e.g., generator, converters) can trigger shutdowns or accelerated wear. | Continuous operation under high load or blocked airflow. | Dust buildup, worn bearings, poor lubrication, overheating due to failed temperature sensors. | 5 | Probability of Data: Moderate (~10–20 % within 10 yrs), higher in dusty/agricultural or offshore sites | 3 | Fan speed and temperature increase show failure quickly. | 105 | Low
| Fire suppression system (sensors, extinguishers) | Sensor false alarms or failure to detect fire | 10 | Extremely critical — if it fails during fire, total turbine loss and safety risk to personnel. | Dust, oil mist, or vibration affecting smoke/heat detectors. | Contamination of sensor optics, wiring faults, poor calibration. | 6 | Probability of Data: Moderate (~10–20 % over 5 years) | 3 | Panel diagnostics detect most faults; physical canister issues require inspection. | 180 | Medium

## 10-point risk matrix
10-Point Risk Matrix
Severity | 10 | [10 empty] | Severity | Minimal (1) | Occurance | Very Remote (1) | Detection | Certain Detection (1)
| 9 | [11 empty] | Very Low (2) |  | Remote (2) |  | Very High (2)
| 8 | [11 empty] | Low (3) |  | Very Unlikely (3) |  | High (3)
| 7 | [11 empty] | Moderate (4) |  | Unlikely (4) |  | Moderately High (4)
| 6 | [11 empty] | Medium (5) |  | Possible (5) |  | Moderate (5)
| 5 | [11 empty] | Elevated (6) |  | Moderately Likely (6) |  | Moderately Low (6)
| 4 | [11 empty] | High (7) |  | Likely (7) |  | Low (7)
| 3 | [11 empty] | Very High (8) |  | Very Likely (8) |  | Very Low (8)
| 2 | [11 empty] | Severe (9) |  | Almost Certain (9) |  | Extemely Unlikely (9)
| 1 | [11 empty] | Critical (10) |  | Inevitable (10) |  | Impossible (10)
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Occurance
Acceptable
Consideration
Need Corrective Action
Needs Immediate Action
|  | 0 - 150 | Low Risk
|  | 151 - 300 | Medium Risk
|  | 300 + | High Risk

## RPN ranked Components
System | Components | S | O | D | RPN | Risk Level
Rotor | Blades | 10 | 7 | 9 | 630 | High
Rotor | Lightning protection system | 10 | 7 | 9 | 630 | High
Tower | Foundation | 10 | 7 | 9 | 630 | High
Tower | Tower structure (steel, concrete, hybrid, lattice) | 10 | 6 | 8 | 480 | High
Auxilary | Hydraulic system (for pitch, yaw, braking) | 10 | 8 | 5 | 400 | High
Main Housing | Gearbox (planetary, helical stages) | 10 | 8 | 5 | 400 | High
Rotor | Pitch drives | 8 | 6 | 8 | 384 | High
Tower | Cable trays | 6 | 8 | 8 | 384 | High
Control & Safety | Backup power systems (batteries, supercapacitors) | 8 | 8 | 6 | 384 | High
Rotor | Blade root | 10 | 4 | 8 | 320 | High
Main Housing | Main shaft (low-speed shaft) | 10 | 4 | 8 | 320 | High
| Components | S | O | D |  | Risk Level
Rotor | Pitch mechanism | 7 | 8 | 5 | 280 | Medium
Main Housing | Yaw system (motors, bearings, brakes) | 9 | 6 | 5 | 270 | Medium
Rotor | Hub | 9 | 4 | 7 | 252 | Medium
Rotor | Lightning protection system | 9 | 3 | 9 | 243 | Medium
Tower | Internal ladders and safety systems | 9 | 3 | 9 | 243 | Medium
Control & Safety | PLC (programmable logic controllers) | 9 | 9 | 3 | 243 | Medium
Electrical | Transformer (step-up, nacelle or tower base) | 10 | 4 | 6 | 240 | Medium
Auxilary | Blade de-icing systems (electrical, hot air) | 8 | 6 | 5 | 240 | Medium
Main Housing | Brake system (disc, hydraulic, emergency) | 7 | 8 | 4 | 224 | Medium
Control & Safety | Wind vane | 7 | 8 | 4 | 224 | Medium
Tower | Platforms/rest stations | 4 | 6 | 9 | 216 | Medium
Control & Safety | Pitch control system | 10 | 5 | 4 | 200 | Medium
Control & Safety | Remote monitoring & communication modules | 6 | 8 | 4 | 192 | Medium
Electrical | Power electronics (converters, rectifiers, inverters) | 9 | 5 | 4 | 180 | Medium
Control & Safety | Yaw control system | 9 | 4 | 5 | 180 | Medium
Auxilary | Fire suppression system (sensors, extinguishers) | 10 | 6 | 3 | 180 | Medium
Electrical | Cabling (high-voltage, control, fiber optic) | 6 | 4 | 7 | 168 | Medium
Control & Safety | Anemometer | 7 | 6 | 4 | 168 | Medium
Main Housing | Bearings | 9 | 6 | 3 | 162 | Medium
| Components | S | O | D |  | Risk Level
Tower | Service lift | 5 | 5 | 6 | 150 | Low
Main Housing | Direct-drive system (if applicable) | 9 | 4 | 4 | 144 | Low
Electrical | Switchgear (circuit breakers, disconnect switches) | 8 | 6 | 3 | 144 | Low
Electrical | Control boards | 7 | 5 | 4 | 140 | Low
Control & Safety | SCADA system | 7 | 9 | 2 | 126 | Low
Main Housing | Generator (SCIG, DFIG, PMSG) | 4 | 6 | 5 | 120 | Low
Tower | Tower lighting (aviation compliance) | 7 | 5 | 3 | 105 | Low
Auxilary | Cooling fans and ventilation | 7 | 5 | 3 | 105 | Low
Main Housing | Cooling system (air/liquid, heat exchangers) | 5 | 6 | 3 | 90 | Low
Main Housing | Lubrication system (oil pumps, filters) | 6 | 5 | 3 | 90 | Low
Auxilary | Heating systems (nacelle heaters) | 5 | 4 | 4 | 80 | Low
Main Housing | Sensors (vibration, temperature, strain, oil quality) | 6 | 6 | 2 | 72 | Low
Control & Safety | Emergency stop buttons | 8 | 4 | 2 | 64 | Low
Main Housing | Gearbox lubrication system | 4 | 5 | 3 | 60 | Low

## SCADA FMEA
FMEA Analysis based on SCADA Relationship Data
System | Components | Failure | Severity | Failure Cause | Root Cause | Occurance | Detection | RPN | Risk Level | Maintenance Procedures | Cost for Maintenance | Cost for replacement
Rotor System | Blades | Leading edge erosion | 10 | rain, hail, sand, and dust erode the blade’s outer coating | High-speed rain/particle impact during normal operation, especially at blade tip speeds of 60–80 m/s | 7 | 9 | 630 | High | LEP renewal, composite repair, cleaning, erosion coating | $500–$40,000 | Blade Replacement: $100,000–$250,000 per blade
| Blade root | Fatigue cracking in root bolts or laminates | 10 | Repeated cyclic loading from wind gusts causes micro-cracks in composite laminates or root bolts/flanges | High‐cycle fatigue from turbulence, frequent start/stop cycles, and yaw misalignment | 4 | 8 | 320 | High | Bolt torque check, NDT, bolt replacement, laminate repair | $1,000–$40,000 | Bolt Set Replacement: $8,000–$20,000
| Hub | Structural cracking of hub casting/welds | 9 | High cyclic bending loads from gusts or rotor imbalance produce micro-cracks in the cast or welded hub body | Casting porosity, residual welding stresses, or operating beyond design wind regime | 4 | 7 | 252 | Medium | NDT, weld repair, reinforcement, stress relief | $3,000–$60,000 | Full Hub Replacement: $100,000–$250,000 + crane costs
| Pitch drives | Gear wear or pitting | 8 | Continuous oscillatory motion of drive gearbox during frequent pitch corrections | Inadequate or degraded grease/oil, misalignment of motor and ring gear, overload from abrupt braking or high turbulence | 6 | 8 | 384 | High | Oil change, gear inspection, gearbox replacement | $1,000–$60,000 | Pitch motor replacement: $8,000–$20,000
Nacelle (Main Housing) | Gearbox (planetary, helical stages) | Gear tooth pitting / micropitting | 10 | High contact stress from continuous torque transmission | Inadequate lubrication film, misalignment of planetary or helical gears, contaminated oil increasing wear particles | 8 | 5 | 400 | High | Oil analysis, oil change, sensor installation, gear repair | $300-$40,000 | Full Gearbox Replacement: $150,000–$350,000 + crane costs
| Gearbox lubrication system | Oil pump failure | 4 | Loss of oil flow or pressure | Pump motor burnout, bearing wear, cavitation from clogged suction strainer, low oil level, or air ingress | 5 | 3 | 60 | Low | Pump replacement, flush, filter change | $3,000-$8,000 | Complete Replacement: $24,000